## cases
Copy cases from IDF editor
0 | Name | B-2 Dairy Case | B-4 Produce Case | B-5 Meat Sales Case | B-6 Deli Sales Case | Rack B ghost case | A-1 Sales Case | A-2 Sales Case | Rack A ghost case
1 | Availability Schedule Name | Always On Sch | Always On Sch | Always On Sch | Always On Sch | Always On Sch | Always On Sch | Always On Sch | Always On Sch
2 | Zone Name | Deli Thermal Zone | Produce Thermal Zone | Sales Thermal Zone | Sales Thermal Zone | Sales Thermal Zone | Sales Thermal Zone | Sales Thermal Zone | Sales Thermal Zone
3 | Rated Ambient Temperature | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
4 | Rated Ambient Relative Humidity | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
5 | Rated Total Cooling Capacity per Unit Length | 6374 | 6374 | 378 | 6374 | 24 | 601 | 601 | 24
6 | Rated Latent Heat Ratio | 0.3 | 0.3 | 0.1 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1
7 | Rated Runtime Fraction | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
8 | Case Length | 3 | 30 | 33.6 | 49.3 | 0.3 | 81.7 | 39 | 0.3
9 | Case Operating Temperature | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | -15 | -12.2 | -15
10 | Latent Case Credit Curve Type | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod
11 | Latent Case Credit Curve Name | OpenMultiShelf_MT_Dairy_LatentCaseCreditCurve | OpenMultiShelf_MT_Dairy_LatentCaseCreditCurve | GlassDoor_LT&MT_General_LatentCaseCreditCurve | OpenMultiShelf_MT_Dairy_LatentCaseCreditCurve | OpenMultiShelf_LT&MT_General_LatentCaseCreditCurve | GlassDoor_LT&MT_General_LatentCaseCreditCurve | GlassDoor_LT&MT_General_LatentCaseCreditCurve | GlassDoor_LT&MT_General_LatentCaseCreditCurve
12 | Standard Case Fan Power per Unit Length | 95.1 | 95.1 | 16.4 | 95.1 | 3.3 | 49.2 | 49.2 | 3.3
13 | Operating Case Fan Power per Unit Length | 95.1 | 95.1 | 16.4 | 95.1 | 3.3 | 49.2 | 49.2 | 3.3
14 | Standard Case Lighting Power per Unit Length | 584 | 584 | 101.7 | 584 | 0 | 39.4 | 39.4 | 0
15 | Installed Case Lighting Power per Unit Length | 584 | 584 | 102 | 584 | 0 | 39 | 39 | 0
16 | Case Lighting Schedule Name | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch
17 | Fraction of Lighting Energy to Case | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0.8 | 0.8 | 0
18 | Case Anti-Sweat Heater Power per Unit Length | 0 | 0 | 0 | 0 | 0 | 249.3 | 249.3 | 0
19 | Minimum Anti-Sweat Heater Power per Unit Length | 0 | 0 | 0 | 0 | 0 | 249.3 | 249.3 | 0
20 | Anti-Sweat Heater Control Type | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant
21 | Humidity at Zero Anti-Sweat Heater Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Case Height
23 | Fraction of Anti-Sweat Heater Energy to Case | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0
24 | Case Defrost Power per Unit Length | 0 | 0 | 0 | 0 | 0 | 1669.9 | 1669.9 | 0
25 | Case Defrost Type | OffCycle | OffCycle | OffCycle | OffCycle | None | ElectricwithTemperatureTermination | ElectricwithTemperatureTermination | None
26 | Case Defrost Schedule Name | B-2 Dairy Case_defrost_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-4 Produce Case_defrost_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-5 Meat Sales Case_defrost_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-6 Deli Sales Case_defrost_3_defrosts_per_day_30_min_plus_0_min_dripdown | Rack B ghost case_defrost_0_defrosts_per_day_0_min_plus_0_min_dripdown | A-1 Sales Case_defrost_1_defrosts_per_day_90_min_plus_0_min_dripdown | A-2 Sales Case_defrost_1_defrosts_per_day_90_min_plus_0_min_dripdown | Rack A ghost case_defrost_0_defrosts_per_day_0_min_plus_0_min_dripdown
27 | Case Defrost Drip-Down Schedule Name | B-2 Dairy Case_dripdown_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-4 Produce Case_dripdown_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-5 Meat Sales Case_dripdown_3_defrosts_per_day_30_min_plus_0_min_dripdown | B-6 Deli Sales Case_dripdown_3_defrosts_per_day_30_min_plus_0_min_dripdown | Rack B ghost case_dripdown_0_defrosts_per_day_0_min_plus_0_min_dripdown | A-1 Sales Case_dripdown_1_defrosts_per_day_90_min_plus_0_min_dripdown | A-2 Sales Case_dripdown_1_defrosts_per_day_90_min_plus_0_min_dripdown | Rack A ghost case_dripdown_0_defrosts_per_day_0_min_plus_0_min_dripdown
28 | Defrost Energy Correction Curve Type | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod
29 | Defrost Energy Correction Curve Name | OpenMultiShelf_MT_Dairy_DefrostEnergyMult | OpenMultiShelf_MT_Dairy_DefrostEnergyMult | GlassDoor_LT&MT_General_DefrostEnergyMult | OpenMultiShelf_MT_Dairy_DefrostEnergyMult | OpenMultiShelf_LT&MT_General_DefrostEnergyMult | GlassDoor_LT&MT_General_DefrostEnergyMult | GlassDoor_LT&MT_General_DefrostEnergyMult | GlassDoor_LT&MT_General_DefrostEnergyMult
30 | Under Case HVAC Return Air Fraction | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Refrigerated Case Restocking Schedule Name | Restocking Display Case Sch | Restocking Display Case Sch | Restocking Display Case Sch | Restocking Display Case Sch | No Restocking Sch | Restocking Display Case Sch | Restocking Display Case Sch | No Restocking Sch
32 | Case Credit Fraction Schedule Name | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch | No Night Curtains Sch
33 | Design Evaporator Temperature or Brine Inlet Temperature | -3.9 | -3.9 | -3.9 | -3.9 | -4 | -23.3 | -20.6 | -24
34 | Average Refrigerant Charge Inventory

## walk-ins
Copy walk-ins from IDF editor
0 | Name | B-1 Bakery Walk-In | B-3 Deli Walk-In | B-7 Sales Walk-In | B-8 Sales Walk-In
1 | Availability Schedule Name | Always On Sch | Always On Sch | Always On Sch | Always On Sch
2 | Rated Coil Cooling Capacity | 1108 | 2214 | 4817 | 44600
3 | Operating Temperature | 2.2 | 2.2 | 2.2 | 2.2
4 | Rated Cooling Source Temperature | -4 | -4 | -4 | -4
5 | Rated Total Heating Power | 0 | 0 | 0 | 0
6 | Heating Power Schedule Name | Walk-In Cooler Heater Sch | Walk-In Cooler Heater Sch | Walk-In Cooler Heater Sch | Walk-In Cooler Heater Sch
7 | Rated Cooling Coil Fan Power | 36 | 71.981 | 156.5714 | 1449.7048
8 | Rated Circulation Fan Power | 0 | 0 | 0 | 0
9 | Rated Total Lighting Power | 37.8 | 75.6 | 164.4 | 1522.2
10 | Lighting Schedule Name | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch | Display Case & Walk-In Lights Sch
11 | Defrost Type | OffCycle | OffCycle | OffCycle | OffCycle
12 | Defrost Control Type | TimeSchedule | TimeSchedule | TimeSchedule | TimeSchedule
13 | Defrost Schedule Name | B-1 Bakery Walk-In_defrost_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-3 Deli Walk-In_defrost_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-7 Sales Walk-In_defrost_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-8 Sales Walk-In_defrost_2_defrosts_per_day_20_min_plus_10_min_dripdown
14 | Defrost Drip-Down Schedule Name | B-1 Bakery Walk-In_dripdown_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-3 Deli Walk-In_dripdown_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-7 Sales Walk-In_dripdown_2_defrosts_per_day_20_min_plus_10_min_dripdown | B-8 Sales Walk-In_dripdown_2_defrosts_per_day_20_min_plus_10_min_dripdown
15 | Defrost Power | 0 | 0 | 0 | 0
16 | Temperature Termination Defrost Fraction to Ice | 0.7 | 0.7 | 0.7 | 0.7
17 | Restocking Schedule Name | Restocking Walk-In Sch | Restocking Walk-In Sch | Restocking Walk-In Sch | Restocking Walk-In Sch
18 | Average Refrigerant Charge Inventory
19 | Insulated Floor Surface Area | 7.1 | 14 | 30.6 | 282.8
20 | Insulated Floor U-Value | 567800 | 567800 | 567800 | 567800
21 | Zone 1 Name | Bakery Thermal Zone | Deli Thermal Zone | Sales Thermal Zone | Sales Thermal Zone
22 | Total Insulated Surface Area Facing Zone 1 | 135.1 | 268.6 | 582 | 5375.6
23 | Insulated Surface U-Value Facing Zone 1 | 0.23 | 0.23 | 0.23 | 0.23
24 | Area of Glass Reach In Doors Facing Zone 1 | 0 | 0 | 0 | 0
25 | Height of Glass Reach In Doors Facing Zone 1 | 0 | 0 | 0 | 0
26 | Glass Reach In Door U Value Facing Zone 1 | 2.27 | 2.27 | 2.27 | 2.27
27 | Glass Reach In Door Opening Schedule Name Facing Zone 1 | Walk-In Reach-In Dr Sch | Walk-In Reach-In Dr Sch | Walk-In Reach-In Dr Sch | Walk-In Reach-In Dr Sch
28 | Area of Stocking Doors Facing Zone 1 | 2 | 2 | 2 | 2
29 | Height of Stocking Doors Facing Zone 1 | 2.1 | 2.1 | 2.1 | 2.1
30 | Stocking Door U Value Facing Zone 1 | 0.23 | 0.23 | 0.23 | 0.23
31 | Stocking Door Opening Schedule Name Facing Zone 1 | Walk-In Stocking Dr Sch | Walk-In Stocking Dr Sch | Walk-In Stocking Dr Sch | Walk-In Stocking Dr Sch
32 | Stocking Door Opening Protection Type Facing Zone 1 | StripCurtain | StripCurtain | StripCurtain | StripCurtain

## case_compressors
Name | Rack_A_Compressor_1 | Rack_A_Compressor_2 | Rack_A_Compressor_3 | Rack_A_Compressor_4 | Rack_A_Compressor_5 | Rack_A_Compressor_6 | Rack_B_Compressor_1 | Rack_B_Compressor_2 | Rack_B_Compressor_3 | Rack_B_Compressor_4 | Rack_B_Compressor_5 | Rack_B_Compressor_6
Refrigeration Compressor Power Curve Name | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv
Refrigeration Compressor Capacity Curve Name | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv
Rated Superheat
Rated Return Gas Temperature | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Rated Liquid Temperature | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rated Subcooling
End-Use Subcategory
Mode of Operation
Transcritical Compressor Power Curve Name
Transcritical Compressor Capacity Curve Name

## walkin_compressors&condensers
| CU1 Grocery Freezer | CU2 Grocery Cooler | CU3 Meat Cooler | CU4 Produce Cooler | CU5 Dry Storage | CU6 FS Freezer | CU7 FS Cooler
Name | CU1 | CU2 | CU3 | CU4 | CU5 | CU6 | CU7 | CU8
Heat Rejection Location | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Zone
Design Compressor Rack COP | 1.7 | 3.7 | 3 | 3.1 | 3.2 | 1.3 | 3.7 | 3.2
Compressor Rack COP Function of Temperature Curve Name | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT
Design Condenser Fan Power | 973 | 1261 | 1261 | 1261 | 973 | 1261 | 1261 | 50
Condenser Fan Power Function of Temperature Curve Name | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT
Condenser Type | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled
Water-Cooled Condenser Inlet Node Name
Water-Cooled Condenser Outlet Node Name
Water-Cooled Loop Flow Type | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow
Water-Cooled Condenser Outlet Temperature Schedule Name
Water-Cooled Condenser Design Flow Rate
Water-Cooled Condenser Maximum Flow Rate
Water-Cooled Condenser Maximum Water Outlet Temperature | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Water-Cooled Condenser Minimum Water Inlet Temperature | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Evaporative Condenser Availability Schedule Name
Evaporative Condenser Effectiveness | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Evaporative Condenser Air Flow Rate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate
Basin Heater Capacity | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Basin Heater Setpoint Temperature | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Design Evaporative Condenser Water Pump Power | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Evaporative Water Supply Tank Name
Condenser Air Inlet Node Name
End-Use Subcategory | General | General | General | General | General | General | General | General
Refrigeration Case Name or WalkIn Name or CaseAndWalkInList Name | CU1 Grocery Freezer | CU2 Grocery Cooler | CU3 Meat Cooler | CU4 Produce Cooler | CU5 Dry Storage | CU6 FS Freezer | CU7 FS Cooler | CU8 2DRS Food Service
Heat Rejection Zone Name | [7 empty] | Kitchen

## condenser
Name | Condenser_1
Rated Effective Total Heat Rejection Rate Curve Name | Condenser_1_Capacity_Curve
Rated Subcooling Temperature Difference
Condenser Fan Speed Control Type | VariableSpeed
Rated Fan Power | 10800
Minimum Fan Air Flow Ratio | 0.2
Air Inlet Node Name or Zone Name
End-Use Subcategory | General
Condenser Refrigerant Operating Charge Inventory
Condensate Receiver Refrigerant Inventory
Condensate Piping Refrigerant Inventory