## cases
* Cases have all been modeled sucessfully. Just need some EMS for the cases.
*this is actually a walk-in type case*
Name | CU8 2DRS Food Service | A01A 8' Coffin Dual Temp | A01B 8' Coffin Dual Temp | A01C Dual Temp Coffin End | A02 14DRS Ice Cream | A03 14DRS Ice Cream | A04 16DRS Ice Cream | A05 14DRS Ice Cream | B01 24' Multi-Deck Produce | B02 12' Multi-Deck Produce | B03 24' Multi-Deck Meat | B04 12' Multi-Deck Meat | B05 11DRS Dairy | B06 9DRS Beer | AB01 2DRS Dairy | AB02 2DRS Dairy | AB03 5DRS Dairy | AB04 4DRS Dairy | AB05 4DRS Dairy | AB06 3DRS Dairy | AB07 2DRS Dairy | AB08 2DRS Dairy | AB09 2DRS Dairy | AB01 2DRS Ice Cream | AB02 2DRS Ice Cream | AB03 5DRS Ice Cream | AB04 4DRS Ice Cream | AB05 4DRS Ice Cream | AB06 3DRS Ice Cream | AB07 2DRS Ice Cream | AB08 2DRS Ice Cream | AB09 2DRS Ice Cream
Availability Schedule Name | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_1 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2 | Dual_Temp_Availability_Schedule_2
Zone Name | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery | Grocery
Rated Ambient Temperature | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
Rated Ambient Relative Humidity | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Rated Total Cooling Capacity per Unit Length | 472 | 312 | 312 | 310 | 463 | 463 | 463 | 463 | 1366 | 1366 | 1366 | 1366 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463
Rated Latent Heat Ratio | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Rated Runtime Fraction | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
Case Length | 1 | 2.4 | 2.4 | 1.8 | 11 | 11 | 12.6 | 11 | 7.3 | 3.7 | 7.3 | 3.7 | 8.7 | 7.1 | 1.6 | 1.6 | 3.9 | 3.9 | 3.1 | 3.1 | 2.4 | 1.6 | 1.6 | 1.6 | 1.6 | 3.9 | 3.9 | 3.1 | 3.1 | 2.4 | 1.6 | 1.6
Case Operating Temperature | 1.11 | -26.11 | -26.11 | -26.11 | -24.44 | -24.44 | -24.44 | -24.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -24.44 | -24.44 | -24.44 | -24.44 | -24.44 | -24.44 | -24.44 | -24.44 | -24.44
Latent Case Credit Curve Type | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod
Latent Case Credit Curve Name | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Open_horizontal_single_deck_latent_case_credit_curve | Open_horizontal_single_deck_latent_case_credit_curve | Open_horizontal_single_deck_latent_case_credit_curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Open_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Open_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Open_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Open_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve | Doored_Multi_Shelf_Vertical_Latent_Case_Credit_Curve
Standard Case Fan Power per Unit Length | 96 | 49.2 | 49.2 | 32.8 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6 | 65.6
Operating Case Fan Power per Unit Length | 28.8 | 14.8 | 14.8 | 9.8 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
Standard Case Lighting Power per Unit Length | 174 | 0 | 0 | 0 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8
Installed Case Lighting Power per Unit Length | 69.6 | 0 | 0 | 0 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
Case Lighting Schedule Name | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night | Refrigerated_Case_Lighting_Schedule_Off_At_Night
Fraction of Lighting Energy to Case | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Case Anti-Sweat Heater Power per Unit Length | 18 | 124.6 | 124.6 | 65.6 | 180.4 | 180.4 | 180.4 | 180.4 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 180.4 | 180.4 | 180.4 | 180.4 | 180.4 | 180.4 | 180.4 | 180.4 | 180.4
Minimum Anti-Sweat Heater Power per Unit Length | 18 | 124.6 | 124.6 | 65.6 | 62.3 | 62.3 | 62.3 | 62.3 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 62.3 | 62.3 | 62.3 | 62.3 | 62.3 | 62.3 | 62.3 | 62.3 | 62.3
Anti-Sweat Heater Control Type | Constant | Constant | Constant | Constant | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | Constant | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod | DewpointMethod
Humidity at Zero Anti-Sweat Heater Energy | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Case Height | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13
Fraction of Anti-Sweat Heater Energy to Case | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Case Defrost Power per Unit Length | 0 | 1364.5 | 1364.5 | 888.9 | 980.7 | 980.7 | 980.7 | 980.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.7 | 980.7 | 980.7 | 980.7 | 980.7 | 980.7 | 980.7 | 980.7 | 980.7
Case Defrost Type | OffCycle | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | OffCycle | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination | HotGaswithTemperatureTermination
Case Defrost Schedule Name | defrost_sch 33 | defrost_sch 1 | defrost_sch 1 | defrost_sch 1 | defrost_sch 2 | defrost_sch 3 | defrost_sch 4 | defrost_sch 5 | defrost_sch 15 | defrost_sch 16 | defrost_sch 17 | defrost_sch 18 | defrost_sch 19 | defrost_sch 20 | defrost_sch 21 | defrost_sch 22 | defrost_sch 23 | defrost_sch 24 | defrost_sch 25 | defrost_sch 26 | defrost_sch 27 | defrost_sch 28 | defrost_sch 29 | defrost_sch 6 | defrost_sch 7 | defrost_sch 8 | defrost_sch 9 | defrost_sch 10 | defrost_sch 11 | defrost_sch 12 | defrost_sch 13 | defrost_sch 14
Case Defrost Drip-Down Schedule Name | defrost_sch 33 | defrost_sch 1 | defrost_sch 1 | defrost_sch 1 | defrost_sch 2 | defrost_sch 3 | defrost_sch 4 | defrost_sch 5 | defrost_sch 15 | defrost_sch 16 | defrost_sch 17 | defrost_sch 18 | defrost_sch 19 | defrost_sch 20 | defrost_sch 21 | defrost_sch 22 | defrost_sch 23 | defrost_sch 24 | defrost_sch 25 | defrost_sch 26 | defrost_sch 27 | defrost_sch 28 | defrost_sch 29 | defrost_sch 6 | defrost_sch 7 | defrost_sch 8 | defrost_sch 9 | defrost_sch 10 | defrost_sch 11 | defrost_sch 12 | defrost_sch 13 | defrost_sch 14
Defrost Energy Correction Curve Type | None | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod | RelativeHumidityMethod
Defrost Energy Correction Curve Name |  | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult |  | None | None | None | None | None | None | None | None | None | None | None | None | None | None | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult | SingleShelfHorizontal_DefrostEnergyMult
Under Case HVAC Return Air Fraction | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigerated Case Restocking Schedule Name | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING
Case Credit Fraction Schedule Name | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS | NO_NIGHT_CURTAINS
Design Evaporator Temperature or Brine Inlet Temperature | -3.89 | -31.67 | -31.67 | -31.67 | -28.33 | -28.33 | -28.33 | -28.33 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -2.78 | -28.33 | -28.33 | -28.33 | -28.33 | -28.33 | -28.33 | -28.33 | -28.33 | -28.33
Average Refrigerant Charge Inventory | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## walk-ins
Name | CU1 Grocery Freezer | CU2 Grocery Cooler | CU3 Meat Cooler | CU4 Produce Cooler | CU5 Dry Storage | CU6 FS Freezer | CU7 FS Cooler
Availability Schedule Name | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON | ALWAYS_ON
Rated Coil Cooling Capacity | 7173 | 4571 | 4219 | 3179 | 14240 | 1325 | 1641
Operating Temperature | -26.11 | 2.22 | -2.22 | 4.44 | 12.78 | -26.11 | 2.22
Rated Cooling Source Temperature | -31.11 | -3.33 | -6.67 | 0.56 | -2.22 | -30 | -2.22
Rated Total Heating Power | 575 | 345 | 345 | 345 | 0 | 575 | 345
Heating Power Schedule Name | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On | WalkIn_Heater_Schedule_Always_On
Rated Cooling Coil Fan Power | 275 | 57 | 48 | 34 | 51 | 34 | 38
Rated Circulation Fan Power | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rated Total Lighting Power | 167 | 167 | 63 | 55 | 265 | 18 | 20
Lighting Schedule Name | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On | Refrigerated_Case_Lighting_Schedule_Always_On
Defrost Type | Electric | OffCycle | Electric | OffCycle | OffCycle | Electric | OffCycle
Defrost Control Type | TemperatureTermination | TimeSchedule | TemperatureTermination | TimeSchedule | TimeSchedule | TemperatureTermination | TimeSchedule
Defrost Schedule Name | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 32 | Defrost_sch 31 | Defrost_sch 33
Defrost Drip-Down Schedule Name | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 31 | Defrost_sch 32 | Defrost_sch 31 | Defrost_sch 33
Defrost Power | 6531 | 0 | 3619 | 0 | 0 | 1622 | 0
Temperature Termination Defrost Fraction to Ice | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Restocking Schedule Name | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING | NO_RESTOCKING
Average Refrigerant Charge Inventory
Insulated Floor Surface Area | 44.22 | 44.22 | 16.72 | 14.52 | 70.23 | 4.88 | 5.43
Insulated Floor U-Value | 0.2 | 3.79 | 3.79 | 3.79 | 3.79 | 0.2 | 3.79
Zone 1 Name | Walkin | Walkin | Walkin | Walkin | Kitchen | Kitchen | Kitchen
Total Insulated Surface Area Facing Zone 1 | 112.04 | 112.04 | 64.38 | 58.65 | 167.32 | 29.13 | 31.02
Insulated Surface U-Value Facing Zone 1 | 0.18 | 0.2 | 0.2 | 0.2 | 0.2 | 0.18 | 0.2
Area of Glass Reach In Doors Facing Zone 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Height of Glass Reach In Doors Facing Zone 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Glass Reach In Door U Value Facing Zone 1 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
Glass Reach In Door Opening Schedule Name Facing Zone 1 | No_Door_Schedule | No_Door_Schedule | No_Door_Schedule | No_Door_Schedule | No_Door_Schedule | No_Door_Schedule | No_Door_Schedule
Area of Stocking Doors Facing Zone 1 | 1.49 | 1.49 | 0 | 0 | 0 | 0 | 2.97
Height of Stocking Doors Facing Zone 1 | 1.22 | 1.22 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44
Stocking Door U Value Facing Zone 1 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
Stocking Door Opening Schedule Name Facing Zone 1 | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE | WALKIN_DOOR_OPEN_SCHEDULE
Stocking Door Opening Protection Type Facing Zone 1 | StripCurtain | StripCurtain | None | None | None | None | StripCurtain
Zone 2 Name
Total Insulated Surface Area Facing Zone 2
Insulated Surface U-Value Facing Zone 2
Area of Glass Reach In Doors Facing Zone 2
Height of Glass Reach In Doors Facing Zone 2
Glass Reach In Door U Value Facing Zone 2
Glass Reach In Door Opening Schedule Name Facing Zone 2
Area of Stocking Doors Facing Zone 2
Height of Stocking Doors Facing Zone 2
Stocking Door U Value Facing Zone 2
Stocking Door Opening Schedule Name Facing Zone 2
Stocking Door Opening Protection Type Facing Zone 2
Zone 3 Name
Total Insulated Surface Area Facing Zone 3
Insulated Surface U-Value Facing Zone 3
Area of Glass Reach In Doors Facing Zone 3
Height of Glass Reach In Doors Facing Zone 3
Glass Reach In Door U Value Facing Zone 3
Glass Reach In Door Opening Schedule Name Facing Zone 3
Area of Stocking Doors Facing Zone 3
Height of Stocking Doors Facing Zone 3
Stocking Door U Value Facing Zone 3
Stocking Door Opening Schedule Name Facing Zone 3
Stocking Door Opening Protection Type Facing Zone 3

## case_compressors
Name | Rack_A_Compressor_1 | Rack_A_Compressor_2 | Rack_A_Compressor_3 | Rack_A_Compressor_4 | Rack_A_Compressor_5 | Rack_A_Compressor_6 | Rack_B_Compressor_1 | Rack_B_Compressor_2 | Rack_B_Compressor_3 | Rack_B_Compressor_4 | Rack_B_Compressor_5 | Rack_B_Compressor_6
Refrigeration Compressor Power Curve Name | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZF33K4E-TWC_R-404A_LOW_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv | ZS38K4E-TF5_R-404A_MED_pwrcurv
Refrigeration Compressor Capacity Curve Name | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZF33K4E-TWC_R-404A_LOW_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv | ZS38K4E-TF5_R-404A_MED_qcurv
Rated Superheat
Rated Return Gas Temperature | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Rated Liquid Temperature | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rated Subcooling
End-Use Subcategory
Mode of Operation
Transcritical Compressor Power Curve Name
Transcritical Compressor Capacity Curve Name

## walkin_compressors&condensers
| CU1 Grocery Freezer | CU2 Grocery Cooler | CU3 Meat Cooler | CU4 Produce Cooler | CU5 Dry Storage | CU6 FS Freezer | CU7 FS Cooler
Name | CU1 | CU2 | CU3 | CU4 | CU5 | CU6 | CU7 | CU8
Heat Rejection Location | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Outdoors | Zone
Design Compressor Rack COP | 1.7 | 3.7 | 3 | 3.1 | 3.2 | 1.3 | 3.7 | 3.2
Compressor Rack COP Function of Temperature Curve Name | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT
Design Condenser Fan Power | 973 | 1261 | 1261 | 1261 | 973 | 1261 | 1261 | 50
Condenser Fan Power Function of Temperature Curve Name | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT | CU_COP_CURVE_CONSTANT
Condenser Type | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled | AirCooled
Water-Cooled Condenser Inlet Node Name
Water-Cooled Condenser Outlet Node Name
Water-Cooled Loop Flow Type | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow | VariableFlow
Water-Cooled Condenser Outlet Temperature Schedule Name
Water-Cooled Condenser Design Flow Rate
Water-Cooled Condenser Maximum Flow Rate
Water-Cooled Condenser Maximum Water Outlet Temperature | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Water-Cooled Condenser Minimum Water Inlet Temperature | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Evaporative Condenser Availability Schedule Name
Evaporative Condenser Effectiveness | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Evaporative Condenser Air Flow Rate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate | autocalculate
Basin Heater Capacity | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Basin Heater Setpoint Temperature | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Design Evaporative Condenser Water Pump Power | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Evaporative Water Supply Tank Name
Condenser Air Inlet Node Name
End-Use Subcategory | General | General | General | General | General | General | General | General
Refrigeration Case Name or WalkIn Name or CaseAndWalkInList Name | CU1 Grocery Freezer | CU2 Grocery Cooler | CU3 Meat Cooler | CU4 Produce Cooler | CU5 Dry Storage | CU6 FS Freezer | CU7 FS Cooler | CU8 2DRS Food Service
Heat Rejection Zone Name | [7 empty] | Kitchen

## condenser
Name | Condenser_1
Rated Effective Total Heat Rejection Rate Curve Name | Condenser_1_Capacity_Curve
Rated Subcooling Temperature Difference
Condenser Fan Speed Control Type | VariableSpeed
Rated Fan Power | 10800
Minimum Fan Air Flow Ratio | 0.2
Air Inlet Node Name or Zone Name
End-Use Subcategory | General
Condenser Refrigerant Operating Charge Inventory
Condensate Receiver Refrigerant Inventory
Condensate Piping Refrigerant Inventory